## BOQ
Mobile Interim Company 2 S.A.L
MIC 2
BIR Hassan Core Site -Estimated BOQ
# | Description | Unit | Estimated Qty | U/Price $ | Total $ | Remarks
1 | Civil works
1 | Demolition works (aluminum walls,false ceiling,duct,..) | L.S | 1 |  |  | in case needed
2 | supply and installation of Gypsum double partition wall withh fire rated boards manufactured according to ASTM C- 36, 12.5mm thick and rockwool filled as per RFP | M2 | 50 |  |  | in case needed
3 | Plastering as per RFP | M2 | 40 |  |  | in case needed
4 | Painting as per RFP | M2 | 40 |  |  | in case needed
5 | supply and insallation of False suspended ceiling similar to the exisiting one as per RFP | M2 | 200 |  |  | in case needed
6 | obsolete cables dismantling and transportation to MIC2 warehouse | L.S | 1 |  |  | in case needed
7 | Supply and installation of external waterproofing | M2 | 50 |  |  | in case needed
8 | Supply and installation of raised floor system including panels, stringers, pedestals… | M2 | 35 |  |  | in case needed
9 | Supply and installation of fresh air damper wiith all related ducts and accessories | L.S | 2 |  |  | in case needed
2 | Mechanical Works
1 | Complete rehabilitation of the generator's area : Fence, Tent , fuel pipes…. | L.S. | 1
2 | Supply and installation of generators monitoring system as per RFP | L.S. | 1
3 | Electrical Works (refer to RFP)
1 | Supply & installation of HDG cable tray 30cm as per RFP | L.m | 100 |  |  | in case needed
2 | Supply & installation of HDG cable basket 30cm as per RFP | L.m | 50 |  |  | in case needed
3 | Supply and installation of fiber runner with all related accessories | L.m | 100 |  |  | in case needed
4 | Supply & installation of outlet sockets (16A) | each | 2 |  |  | in case needed
5 | Supply and installation of new LED lighting lamps as per the RFP (Swap exisiting NEON lamp) | each | 50 |  |  | in case needed
6 | Supply and installation of a new emergency light similar to the exisiting | each | 5 |  |  | in case needed
7 | Supply & installation of grounding system (connection) | each | 1 |  |  | in case needed
8 | Supply & installation of power cable (3x240mm+N) cable NYM as per RFP | L.m | 250 |  |  | in case needed
9 | Supply & installation of power cable (3x25mm+N) cable NYM as per RFP | L.m | 100 |  |  | in case needed
10 | Supply & installation of power cable (3x16mm+N) cable NYM as per RFP | L.m | 100 |  |  | in case needed
11 | Supply & installation of power cable (3x10mm+N) cable NYM as per RFP | L.m | 100 |  |  | in case needed
12 | Supply & installation of power cable (3x6mm+N) cable NYM as per RFP | L.m | 100 |  |  | in case needed
13 | Supply & installation of power cable (2x10mm) cable as per RFP | L.m | 100 |  |  | in case needed
14 | Supply & installation of power cable (2x2.5mm) cable as per RFP | L.m | 200 |  |  | in case needed
15 | Grounding cables 240mm | L.m | 100 |  |  | in case needed
16 | Supply & installation of ATS 1000 amp solution system with complete cabling as per the RFP | each | 2
17 | Supply & installation of temporary ATS 1000 amp with complete cabling (3 inputs) | each | 1
18 | supply and installation of Industrial sockets (32A) as per RFP | each | 32
19 | supply and installation of Industrial sockets (16A) as per RFP | each | 32
20 | Supply of spare parts as per Appendix 1 (ATS section, related to new installation only) | L.S | 1
4 | Comfortable cooling AC
1 | Supply & installation of split duct type A/C unit 5T as per RFP | each | 2 |  |  | 2 units will need 2 elbows and double deflection grill for vertical installation and insulated drainage pans
2 | Supply and installation of complete mechanical fittings for split type units(copper piping,control cable , ducts, diffusers, grills, cable trays where needed, insulation where needed) | L.m. | 120 |  |  | where needed
6 | Supply and installation on units drainage system 1" PVC (connection with the exisiting one) | Lm | 20
7 | Dismantling of old 5T units and transportation to MIC 2 warehouse | L.S | 1
8 | Supply of spare parts requested in Appendix 1 (cooling section) | L.S | 1
5 | Fire Protection
1 | supply & installation of FM200 fire cylinder with 372 LB of agent (mechanical fittings with manual switch, reserve) same as existing. | each | 1
2 | supply & installation of FM200 fire cylinder with 161 LB of agent (mechanical fittings with manual switch, reserve) same as existing. | each | 1
3 | supply & installation of FM200 fire cylinder with 94 LB of agent (mechanical fittings with manual switch, reserve) same as existing. | each | 1
4 | supply & installation of FM200 fire cylinder with 83 LB of agent (mechanical fittings with manual switch, reserve) same as existing. | each | 1
5 | supply & installation of FM200 fire cylinder with 69 LB of agent (mechanical fittings with manual switch, reserve) same as existing. | each | 1
6 | supply & installation of FM200 fire cylinder with 37.5 kg of agent (mechanical fittings with manual switch, reserve) same as existing. | each | 1
7 | Integrity test execution | each | 1
6 | UPS
1 | Supply & installation of UPS system (60 kW) with complete cabling from the source (MDB breaker) to the last terminal (PDU or UPSDB) as per the RFP | each | 2 |  |  | UPS with built in batteries is acceptable
2 | Supply & installation of UPS battery banks with adequate calculation of 15 min autonomy on 30kw load as per the RFP | each | 2
3 | Supply and installation of batteries steel frame | Kg | 500 |  |  | in case needed
4 | Supply and installation of UPSDB with complete adequate cabling. Input breaker size to be selected as per UPS manufacturer recommendation DB type 1B wall mounted panel (48 modules with minimum 24 breakers (1x32A,10kA)) Factory assembled, equipped with phase indicating lights; bottom cable entry only | each | 2 |  |  | 2 different colors (charcoal satin and blue for example)
5 | Supply & installation of high standard smart UPS 0U PDUs (with at least 20xC13, 4x C19 outlets with complete cabling from the source PDF to the last terminal (including server cables where needed) | each | 16
6 | Supply of spare parts as per Appendix 1 (UPS section) | L.S | 1
7 | Communications
1 | Supply, installation, testing and commissioning of complete Communication cabinets, racks and enclosures with all necessary accessories, wiring and power cables with dual smart 0U PDUS ans command sockets (IEC 60309) etc. in accordance with specification and drawings as required to delivery a complete and functioning system. | each | 1
2 | Network Floor mounted Cabinet (bearing capacity of 1200kg) (800x1200x2000mm) | each | 1
3 | Public Address Floor mounted Cabinet (bearing capacity of 1200kg) (600x1200x2000mm) | each | 7
4 | Cable Management panel 1 RU | each | 16
TOTAL